# UNIT III

WATER TREATMENT GENERAL INTRODUCTION

Water available in various sources contains various types of impurities and cannot

be directly used by the public for various purposes, before removing the impurities. For potability water should be free from unpleasant tastes, odours and must have sparkling appearance. The water must be free from disease-spreading germs. The amount and type of treatment process will depend on the quality of raw water and the standards of quality of raw water and the standards of quality to be required after treatment as per the table No.

The surface sources generally contains large amount of impurities therefore they requires sedimentation, filtration and chlorination as treatment. If the water contains algae or other micro organisms, pre chlorination has to be done tastes and odours , dissolved gases like CO2, H2S are removed by aeration. During the flood season , the turbidity of the surface water may be high and flocculation may become necessary to remove turbidity.

Ground water which are usually clear may require only disinfection and chemical treatment for the removal of pathogens, Iron removal, Softening etc.

Sometimes ground water contains dissolved gases like hydrogen sulphide (H2S)

carbon dioxide (CO2), which gives very bad odour and requires its removal by aeration.

# TREATMENT UNIT FLOW DIAGRAM

Water treatment includes many operations like Aeration, Flocculation,

Sedimentation, Filtration, Softening, Chlorination and demineralization. Depending upon the quality of raw water and the quality of water desired. Several combinations of the above processes may be adopted as shown in the flow diagram.

- When turbidity of water is less than 10 N.T.U Raw Water Treated water for supply GROUND WATER

CHLORINATION

Raw Water Treated water for supply

# SURFACE WATER

THE LOCATION OF TRETMENT PLANT

One complete water treatment plant requires the following process starting from the source of water upto the distribution zone in order of sequence.

# Sl.No. Name of the unit Purpose

  - Intake work including pumping plant Raw water from the source for treatment

  - Plain sedimentation To remove suspended impurities such as silt, clay, sand etc.

  - Sedimentation with coagualtion To remove the suspended matter

  - Filtration To remove microorgans and colloidal matter

  - Water softening plant To remove hardness of water

  - Miscellaneous treatment plants To remove dissolved gases, tastes

and odours.

  - Disinfection To remove pathogenic bacteria

  - Clear water reservoir To store the treated water

  - Pumps for pumping the water in service reservoirs

If town or city is situated at higher elevation then pumping is required.

  - Elevated or underground service reservoir

The following points should be kept in mind while giving layout of any treatment plant.

- The W.T.P. should be located as near to the town so as to avoid the contamination.

- All the units of plant should be located in order of sequence and flow from one unit to other by gravity.

- All the units are arranged in such a way that minimum area is required so as to reduce the cost of construction.

- Sufficient area should be reserved for the future expansion

- Staff quarters and office should be provided near the treatment plants so that the operators can watch the plants easily.

- The site of treatment plant should be very neat and give very good asthetic appearance.

# SCREENING

Screens are fixed in the intake works or at the entrance of treatment plant so as to remove the floating matters as leaves, dead animals etc.

# SEDIMENTATION

It is the process in which the suspended solids are made to settle by gravity under still water conditions is called plain sedimentation.

# PLAIN SEDIMENTATION

By plain sedimentation the following are the advantages.

- Plain sedimentation lightens the load on the subsequent process.

- The operation of subsequent purification process can be controlled in better way.

- The cost of cleaning the chemical coagulation basins is reduced.

- No chemical is lost with sludge discharged from the plain settling basin.

- Less quantity of chemicals are required in the subsequent treatment processes. The amount of matter removed by sedimentation tank depends upon the factors.

- Velocity of flow

- size and shape of particles

- Viscosity of water

The particles which do not change in size, shape or mass during settling are known as the discrete particles. The velocity of descrete particles with dia less than 0.1 mm is given by V = 418 (S - S1) d2 (3T + 70)

(1) 100

Where V → Velocity of settlement in mm/sec S → Specific gravity of the particle

S1 → Specific gravity of water

D → dia of the particle in mm T → Temperature in °C

If the dia of the particle is greater than 0.1mm then the velocity is measured by

V = 418 (S - S1) d (3T + 70)

(2)

100

In practice settling of the particles governed by the resultant of horizontal velocity of water and the verticle downward velocity of the particle. The path of the settling particle is as shown in Fig 5.2.

# DESIGN ASPECTS OF SEDIMENTATION TANKS

The design aspects of sedimentary tanks are

- Velocity of flow

- Capacity of tank

- Inlet and outlet arrangements

- Shapes of tanks

- Miscellaneous considerations.

- Velocity of flow: The velocity of flow of water in sedimentation tanks should be sufficient enough to cause the hydraulic subsidence of suspended impurities. It should remain uniform throughout the tank and it is generally not allowed to exceed 150mm to 300mm per minute.

- Capacity of tank: capacity of tank is calculated by i) detension period

ii) Overflow rate

- Detension period: The theoretical time taken by a particle of water to pass between entry and exit of a settling tank is known as the known as the detention period. The capacity of tank is calculated by

C = Q x T where C → Capacity of tank Q → Discharge or rate of flow

T → Detension period in hours

The detention period depends on the quality of suspended impurities present in water. For plain sedimention tanks, the detension period is found to vary from 4 to 8 hours.

- Overflow Rate: in this method it is assumed that the settlement of a particle at the bottom of the settlement of a particle at the bottom of the tank doesnot depend on

the depth of tank and depends upon the surface area of the tank. Distance of descend D

Detension period, T = Velocity of descend V C

But, T = 	(2) Q

From (1) & (2) C D

=	 Q V

D.Q D x Q Q

= 	(1)

Surface overflow rate, V = ------ = ----------- = ---------

C L x B x D L x B

Where L → Length of tank B → Breadth of tank

D → Depth of tank = Side water depth = S.W.D C → Capacity of tank

T → Detention period

U → Discharge or rate of flow

V → Velocity of descend of a particle to the bottom of tank

= Surface overflow rate = S.O.R

# INLET AND OUTLET ARRANGEMENTS

The inlet is a device, which is provided to distribute the water inside a tank, and the outlet is a device, which is meant to collect outgoing water. These arrangements Water Supply Engineering

- 45 -

should be properly designed and located in a such a way that they do not form any obstruction or cause any disturbance to the flowing water.

# SHAPES OF TANKS

Following are the three shapes of settling tank.

  - Rectangular tanks with horizontal flow

  - Circular tanks with radial or spiral flow

  - Hopper bottom tanks with vertical flow

The following are the parameters for satisfactory performance.

- Detention period	3 to 4 hours for plain settling

2 to 21/2 hours for coagulant settling 1 to 11/2 hours for up flow type

- Overflow rate	30 – 40 m3/m2/day for horizontal flow

40-50m3/m2/day for up flow

- Velocity of flow…	0.5 to 1.0 cm/sec

- Weir loading	300m3/m/day

5. L:B	1:3 to 1:4

Breadth of tank…	(10 to 12m) to 30 to 50m

- Depth of tank…	21/2 – 4m

- Dia of circular tank…. upto 60m

- Solids removal efficiency	50%

- Turbidity of water after sedimentation – 15 to 20 N.T.U.

- Inlet and Oulet zones	0.75 to 1.0m

- Free board…	0.5m

- Sludge Zone	0.5m

# SEDIMENTATION AIDED WITH COAGULATION

When water contains fine clay and colloidal impurities which are electrically charged are continually in motion and never settle down due to gravitational force.

Certain chemicals are added to the water so as to remove such impurities which are not removed by plain sedimentation. The chemical form insoluble, gelatinous, flocculent precipitate absorbs and entagle very fine suspended matter and colloidal impurities

during its formation and descent through water. These coagulants further have an advantage of removing colour, odour and taste from the water. Turbidity of water reduced upto 5-10 ppm and bacteria removes upto 65%.

The following are the mostly used Coagulants with normal dose and PH values required for best floc formation .

# Sl.No. Coagulant PH Range Dosage mg/l

- Aluminium sulphate Al2(SO4)3, 18 H2O 5.5 – 8.0 5 – 85

- Sodium Aluminate, Na2Al2O4 5.5 – 8.0 3.4 – 34

- Ferric Chloride (Fecl3) 5.5 – 11.0 8.5 – 51

4. Ferric Sulphate Fe2 (SO4)3 5.5 – 11.0 8.5 – 51

5. Ferric Sulphate FeSO47H2O 5.5 – 11.0 8.5 - 51

Coagulants are chosen depending upon the PH of water. Alum or Aluminium sulphate is normally used in all treatment plants because of the low cost and ease of storage as solid crystals over long periods.

The dosage of coagulants, which should be added to the water, depends upon kind

of coagulant, turbidity of water, colour of water, PH of water, temperature of water and temperature of water and mixing & flocculation time. The optimum dose of coagulant required for a water treatment plant is determined by a Jar test as shown in Fig 5.2.

For starting the experiment first of all the sample of water is taken in every jar and added the coagulant in a jar in varying amounts. The quantity of coagulant added in each jar is noted. Then with the help of electric motar all the paddles are rotated at a speed of 30-40 R.P.M. for about 10 minutes. After this the speed is reduced and paddles are

rotated for about 20-30 minutes. The rotation of paddles is stopped and the floc formed in each Jar is noted and is allowed to settle. The dose of coagulant which gives the best floc is the optimum dose of coagulants.

The coagulants may be fed or allowed to enter either in powder form called dry

feeding or in solution form called wet feeding. The mixing of coagulant with the water to form the floc by the following methods.

- Centrifugal pump

- compressed air

- hydraulic jump

- mixing channel

- mixing basins with buffle walls

- Mixing basins with mechanical means

Now a days some firms manufacture combined unit comprising of feeding,

mixing, flocculator and clarifier device. The Fig 5.2 shows used for sedimentation with coagulation.

# Sedimention with Caogulation

Water enters in this tank through central inlet pipe placed inside the deflector box. The deflector box deflects the water downwards and then it goes out through the holes provided sides of the deflector box. The water flows radially from the deflector box

towards the circumference of the tank, where outlet is provided on the full periphery as shown in the Fig. All the suspended particles along with floc settle down on the slopy floor and clear water goes through outlet. The sludge is removed by scrapper which continuously moves around the floor with very small velocity.

Disinfection and repainting is to be carried out once in ayear before mansoon.

Sludge pipes are to be flushed and kept clean. Bleaching powder may be used to control the growth of algae on the weirs. Scraper mechanism should be oiled and greased periodically.

# FILTRATION

The process of passing the water through beds of sand or other granular materials

is known as filtration. For removing bacteria, colour, taste, odours and producing clear and sparkling water, filters are used by sand filtration 95 to 98% suspended impurities are removed.

# THEORY OF FILTRATION

The following are the mechanisms of filtration

- Mechanical straining – Mechanical straining of suspended particles in the sand pores.

- Sedimentation – Absorption of colloidal and dissolved inorganic matter in the surface of sand grains in a thin film

- Electrolytic action – The electrolytic charges on the surface of the sand particles, which opposite to that of charges of the impurities are responsible for binding

them to sand particles.

- Biological Action – Biological action due to the development of a film of microorganisms layer on the top of filter media, which absorb organic impurities. Filtration is carries out in three types of filters

- Slow sand filter

- Rapid sand filter Gravity filters

- Pressure filter

# SLOW SAND FILTER

Slow sand filters are best suited for the filtration of water for small towns. The

sand used for the filtration is specified by the effective size and uniformity coefficient . The effective size, D10, which is the sieve in millimeters that permits 10% sand by weight

to pass. The uniformity coefficient is calculated by the ratio of D60 and D10.

# CONSTRUCTION

Slow sand filter is made up of a top layer of fine sand of effective size 0.2. to

0.3mm and uniformity coefficient 2 to 3 . The thickness of the layer may be 75 to 90 cm. Below the fine sand layer, a layer of coarse sand of such size whose voids do not permit the fine sand to pass through it. The thickness of this layer may be 30cm. The lowermost layer is a graded gravel of size 2 to 45mm and thickness is about 20 to 30cm. The gravel is laid in layers such that the smallest sizes are at the top. The gravel layer is the retains for the coarse sand layer and is laid over the network of open jointed clay pipe or concrete pipes called under drainage. Water collected by the under drainage is passed into the out chamber

# OPERATION

The water from sedimentation tanks enters the slow sand filter through a submersible inlet as shown in fig 5.3 This water is uniformily spread over a sand bed

without causing any disturbances. The water passes through the filter media at an average rate of 2.4 to 3.6 m3/m2/day. This rate of filtration is continued until the difference between the water level on the filter and in the inlet chamber is slightly less than the depth of water above the sand. The difference of water above the sand bed and in the outlet chamber is called the loss of head.

During filtration as the filter media gets clogged due to the impurities, which stay

in the pores, the resistance to the passage of water and loss of head also increases. When the loss of head reaches 60cm, filtration is stopped and about 2 to 3 cms from the top of bed is scrapped and replaced with clean sand before putting back into service to the filter. The scrapped sand is washed with the water, dried and stored for return to the filter at the time of the next washing . The filter can run for 6 to 8 weeks before it becomes necessary to replace the sand layer.

# USES

The slow sand filters are effective in removal of 98 to 99% of bacteria of raw

water and completely all suspended impurities and turbidity is reduced to 1 N.T.U. Slow sand filters also removes odours, tastes and colours from the water but not pathogenic bacteria which requires disinfection to safeguard against water-borne diseases. The slow sand filters requires large area for their construction and high initial cost for establishment. The rate of filtration is also very slow.

# MAINTENANCE

The algae growth on the overflow weir should be stopped. Rate of filtration

should be maintained constant and free from fluctuation. Filter head indicator should be in good working condition. Trees around the plant should be controlled to avoid bird droppings on the filter bed, No coagulant should be used before slow sand filtration since the floc will clog the bed quickly.

# RAPID SAND FILTER

Rapid sand filter are replacing the slow sand filters because of high rate of

filtration ranging from 100 to 150m3/m2/day and small area of filter required. The main features of rapid sand filter are as follows.

The main features of rapid sand filter are as follows Effective size of sand - 0.45 to 0.70mm

Uniformity coefficient of sand - 1.3 to 1.7 Depth of sand - 60 to 75cm

Filter gravel - 2 to 50mm size (Increase size towards bottom) Depth of gravel - 45cm

Depth of water over sand during filtration - 1 to 2m Overall depth of filter

including 0.5m free board - 2.6m

Area of single filter unit - 100m2 in two parts of each 50m2 Loss of head - Max 1.8 to 2.0m

Turbidity of filtered water - 1 NTU

# OPERATION

The water from coagulation sedimentation tank enters the filter unit through inlet

pipe and uniformily distributed on the whole sand bed. Water after passing through the sand bed is collected through the under drainage system in the filtered water well. The outlet chamber in this filter is also equipped with filter rate controller. In the beginning the loss of head is very small. But as the bed gets clogged, the loss of head increases and the rate of filtration becomes very low. Therefore the filter bed requires its washing.

# WASHING OF FILTER

Washing of filter done by the back flow of water through the sand bed

First the value ‘A’ is closed and the water is drained out from the filter leaving a few centimeter depth of water on the top of sand bed. Keeping all values closed the

compressed air is passed through the separate pipe system for 2-3 minutes, which agitates the sand bed and stirrer it well causing the loosening of dirt, clay etc. inside the sand bed. Now value ‘C’ and ‘B’ are opened gradually, the wash water tank, rises through the laterals, the strainers gravel and sand bed. Due to back flow of water the sand expands and all the impurities are carried away with the wash water to the drains through the channels, which are kept for this purpose.

# CONSTRUCTION

Rapid sand filter consists of the following five parts

- Enclosure tank – A water tight tank is constructed either masony or concrete

- Under drainage system – may be perforated pipe system or pipe and stracher system

- Base material – gravel should free from clay, dust, silt and vegetable matter. Should be durable, hard, round and strong and depth 40cm.

- Filter media of sand – The depth of sand 60 to 75cm

- Appartenances – Air compressors useful for washing of filter and wash water troughs for collection of dirty water after washing of filter.

Washing process is continued till the sand bed appears clearly. The eashing of

filter is done generally after 24 hours and it takes 10 minutes and during back washing the sand bed expands by about 50%.

Rapid sand filter bring down the turbidity of water to 1 N.T.U. This filter needs

constant and skilled supervision to maintain the filter gauge, expansion gauge and rate of flow controller and periodical backwash.

# Comparision of slow sand filter and rapid sand filter Sl.No. ITEM S.S.F R.S.F

- Area Need very large area Needs small area

- Raw Water Turbidity

Not more than 30 NTU Not more than 10NTU hence needs coagulation

- Sand Media Effective size 0.2 to 0.3 mm uniformity coefficient

2 to 3 single layer of uniform size

Effective size 0.45 to 0.7 mm uniformity coefficient

1.3 to 1.7 multiple graded

layers of sand.

- Rate of Filtration

2.4 to 3.6m3/m2/day 100-150 m3/m2/day

- Loss of Head 0.6m to 0.7 m 1.8m to 2.0m

- Supervision No skilled supervision is required

Skilled supervision is required

- Cleaning of Filter

Scraping of 21/2cm thick layer washing and replacing. Cleaning interval that is replacement of sand at 1 to 2 months.

Back wash with clean water under pressure to detach the dirt on the sand.

Backwashing daily or on alternate days.

- Efficiency Bacterial removal, taste, odour, colour and turbidity

removal.

There is no removal of bacteria. Removal colour taste, odour and turbidity is good.

# PRESSURE FILTER

Pressure filter is type of rapid sand filter in a closed water tight cylinder through which the water passes through the sand bed under pressure. All the operations of the

filter is similar to rapid gravity filter, expect that the coagulated water is directly applied to the filter without mixing and flocculation. These filters are used for industrial plants but these are not economical on large scale.

Pressure filters may be vertical pressure filter and horizontal pressure filter. The

Fig 5.5 shows vertical pressure filter. Backwash is carried by reversing the flow with values. The rate of flow is 120 to 300m3/m2/day.

# ADVANTAGES

- It is a compact and automatic operation

- These are ideal for small estates and small water works

- These filters requires small area for installation

- Small number of fittings are required in these filters

- Fitered water comes out under pressure no further pumping is required.

- No sedimentation and coagulant tanks are required with these units.

# DISADVATAGES

- Due to heavy cost on treatment , they cannot be used for treatment large quantity of water at water works

- Proper quality control and inspection is not possible because of closed tank

- The efficiency of removal of bacteria & turbidity is poor.

- Change of filter media, gravel and repair of drainage system is difficult.

# DISINFECTION OF WATER

The process of killing the infective bacteria from the water and making it safe to

the user is called disinfection. The water which comes out from the filter may contain some disease – causing bacteria in addition to the useful bacteria. Before the water is supplied to the public it is utmost necessary to kill all the disease causing bacteria. The chemicals or substances which are used for killing the bacteria are known as disinfectants.

# REQUIREMENTS OF GOOD DISINFECTANTS

- They should destroy all the harmful pathogens and make it safe for use,.

- They should not take more time in killing bacteria

- They should be economical and easily available

- They should not require high skill for their application

- After treatment the water should not become toxic and objectionable to the user.

- The concentration should be determined by simply and quickly.

# METHODS OF DISINFECTION

Disinfection of water by different physical and chemical methods

# PHYSICAL METHODS

- BOILING : Boil the water for 15 to 20 minutes and kills the disease causing bacteria. This process is applicable for individual homes.

- ULTRA-VIOLET RAYS: Water is allowed to pass about 10cm thickness by ultraviolet rays. This process is very costly and not used at water works. Suitable for institutions.

- ULTRASONIC RAYS: Suitable for institutions.

# CHEMICAL METHODS

    - CHLORINATION : Using chlorine gas or chlorine compounds.

    - BROMINE AND IODINE : It is expensive and leaves taste and odour.

    - POTASSIUM PERMANGANATE: This method is used for disinfection of dug well water, pond water or private source of water.

    - OZONE : Very expensive process, leaves no taste, odour or residual.

    - EXCESS LIME TREATMENT: Needs long detension time for time interval and large lime sludges to be treated.

# CHLORINATION

Chlorination is the addition of chlorine to kill the bacteria Chlorination is very widely adopted in all developing countries for treatment of water for public supply. Chlorine is available in gas, liquid or solid form (bleaching powder) ADVANTAGES OF CHLORINE

- Chlorine is manufactured easily by electrolytes of common salts (NaCl)

- It is powerful oxidant and can penetrate the cell wall of organism and its contents.

- Dosage can be controlled precisely

- can be easily detected by simple orthotolidine test

- Doesnot form harmful constituents on reaction with organics of inorganics in water

- leaves required residue in water to neutralise recontamination later.

# PRECAUTIONS IN USING CHLORINE

- Chlorine gas or liquid is highly corrosive and Lithal to Inhale. Hence it is to be stored carefully in sealed container at a distance.

- If the water contains phenolic compounds, there is a reaction with chlorine can result in cancer causing substances.

# RESIDUAL CHLORINE AND CHLORINE DEMAND

When chlorine is applied in water some of it is consumed in killing the pathogens, some react organs & inorganic substances and the balance is detected as “Residual

Chlorine”. The difference between the quantity applied per litre and the residual is called “Chlorine Demand”. Polluted waters excert more chlorine demand. If water is pre-treated by sedimentation and aeration, chlorine demand may be reduced. Normally residual chlorine of 0.2 mg/litre is required.

# BEHAVIER OF CHLORINE IN WATER

When chlorine is dissolved in water forms hypo chlorous acid and hydro chloric acid. Cl2 + H2O → HOCl + HCl	(1)

After some time hydo chlorous acid further Ionizes as follows HOCl ←→ H+ + OCl	(2)

The two prevailing species (HOCl) and (OCl -) are called free available chlorine are responsible for the disinfection of water.

Clorine reacts with ammonia in water to form Monochloramine, (NH2Cl), dichloramine (NHCl2) and trichloramine , (NCl3) released and their distribution depends on the PHvalue

of water.

# DOSAGE OF CHLORINE

- PLAIN CHLORINATION

Plain chlorination is the process of addition of chlorine only when the surface water with no other treatment is required. The water of lakes and springs is pure and can be used after plain chlorination. A rate of 0.8 mg/lit/hour at 15N/cm2 pressure is the normal dosage so as to maintain in a resided chlorine of 0.2 mg/lit.

# SUPER CHLORINATION

Super chlorination is defined as administration of a dose considerably in excess of that necessary for the adequate bacterial purification of water. About 10 to 15 mg/lit is applied with a contact time of 10 to 30 minutes under the circumstances such as during epidemic breakout water is to be dechlorinated before supply to the distribution system.

# BRAKE POINT CHLORINATION

When chlorine is applied to water containing organics, micro organisms and ammonia the residual chlorine levels fluctuate with increase in dosage

Upto the point B it is obsorbed by reducing agents in water (like nitrates, Iron etc) further increases forms chloramines with ammonia in water. Chloramines are effective as CL and OCL formed. When the free chlorine content increases it reacts with the chloramines and reducing the available chlorine. At the point ‘D’ all the chloramines are converted to effective N2, N2O and NCl3. Beyond point ‘D’ free residual chlorine appear again. This point ‘D’ is called break point chlorination.

Dosage beyond this point is the same as super chlorination. In super chlorination no such rational measurement is made and the dosage is taken at random.

# DECHLORINATION

Removal of excess chlorine resulting from super chlorination in part or completely is called ‘Dechlorination’. Excess chlorine in water gives pungent smell and corrode the pipe lines. Hence excess chlorine is to be removed before supply.

Physical methods like aeration, heating and absorption on charcoal may be adopted. Chemical methods like sulphur dioxide (SO2) , Sodium Bi-sulphate (NaHSO3), Sodium Thiosulphate(Na2S2O8) are used.

# POINTS OF CHLORINATION

Chlorine applied at various stages of treatment and distribution accordingly they are known as pre, post and Re-chlorination.

# PRE-CHLORINATION

Chlorine applied prior to the sedimentation and filtration process is known as Prechlorination.

This is practiced when the water is heavily polluted and to remove

taste, odour, colour and growth of algae on treatment units. Pre-chlorination improves coagulation and post chlorination dosage may be reduced.

# POST CHLORINATION

When the chlorine is added in the water after all the treatment is known as Postchlorination.

# RE-CHLORINATION

In long distribution systems, chlorine residual may fall tendering the water unsafe. Application of excess chlorine to compensate for this may lead to unpleasant smell to consumers at the points nearer to treatment point in such cases chlorine is applied again that is rechlorinated at intermediate points generally at service reservoirs and booster pumping stations.

# DEFLUORIDATION – BY NALGONDA TECHNIQUE

Defluoridation is process of removal of excess fluoride present in the water. The

excess fluoride in the water causes dental abnormalities, hypertension, peptic ulcer, Skin infections, defective vision, coronary thrombosis etc. The permissible level of fluoride in the water is 1mg/litre.

# METHODS OF REMOVAL

- Activated carbons prepared from various materials can be used.

- Lime – soda process of water softening removes fluorides also along with magnesium

- The materials like calcium phosphate, bone charcoal, synthetic tricalcium phosphate a may remove excess fluoride.

- the water may be allowed to pass through filter beds containing floride retaining materials.

In this technique, sodium aluminate or lime, bleaching powder and filter alum are added to fluoride water in sequence. The water is stored for ten minutes and settled for one hour and the water is then withdrawn without disturbing the sediments. The sodium aluminate or lime accelerates the settlement of precipitate and bleaching powder ensures disinfection. The alum dose required will depend upon the concentration of fluorides, alkanity and total dissolved solids in the raw water. It is found that this technique is

simple in operation and economical. It can be used with advantage in villages either on an individual scale or on a mass scale.

# SUMMARY

- Water treatment processes are

a. Sedimenattion b. Filtration c. Disinfection

- Sedimentation is for removal of suspended solids in the water. In plain sedimentation 30

to 40% of solids are removed with detention period of 3 hours. In coagulent aided with sedimentation removes colloids and suspended solids upto 70% with a detention period of 2 – 21/2 hours. Coagulants used are alum, Sodium aluminate, ferric chloride, etc. and Jar test is used to determine cosgulant dosage.

- Filtration is the process of passing the water through sand medium. In slow sand filter the effective size of sand used is 0.2 to 0.3 mm and removes bacteria (90%) , colour , turbidity , taste and odour . Rate of filtration is 2.5 to 3.6 m3/m2/day . In rapid sand filter the effective size of sand used is 0.45 to 0.7 mm . It can not remove bacteria. Colour , odour, taste and turbidity can be removed . For cleaning of rapid sand filter back washing is used. Pressure filter is the same as rapid sand filter excepting the filtration is carried at high pressure.

- Disinfection is the process of killing of pathogenic bacteria by the methods of boiling, U.V.rays, chlorine, bromine, iodine, excess lime, Ozone, Potassium permanganate. Residual chlorine of 0.2 mg/litre is required to safeguard against contamination of water during distribution.

# SHORT ANSWER QUESTIONS

- Define sedimentation.

- What are the advantages of sedimenatation?

- State the factors that effect sedimentation.

- What is meant by coagulation?

- State any four coagulants.

- State any two mechanisms involved in filtration.

- What is negative head in the filtration?

- State any four methods of disinfection of water.

- State any two advantages of chlorination.

- Define Residual Chlorine.

- What is disinfection of water?

- What is meant by dechlorination?

- Name any four diseases caused by excess presence of fluoride in water.

- Define pre chlorination.

- Define post chlorination.

# ESSAY TYPE QUESTIONS

- What are the points to be considered for locating a treatment plant?

- Explain slow sand filter with neat slatch.

- Explain working of rapid sand filter with the help of neat sketch.

- List out the requirements of good disinfectant.

- What do you understand by break point chlorination?

- What are the differences of slow sand filter and rapid sand filter?

- What are the effects of fluorine? How you remove the fluorine by Nelgonda Technique.

- Explain a) pre-chlorination b) post-chlorination

c) de-chlorination c) re-chlorination

- Explain the backwashing of rapid sand filter.