## UNIT IV ADVANCED WATER TREATMENT

Aeration

- Aeration removes odour and tastes due to volatile gases like hydrogen sulphide and due to algae and related organisms.

- Aeration also oxidise iron and manganese, increases dissolved oxygen content in water, removes CO2 and reduces corrosion and removes methane and other flammable gases.

- Principle of treatment underlines on the fact that volatile gases in water escape into atmosphere from the air-water interface and atmospheric oxygen takes their place in water, provided the water body can expose itself over a vast surface to the atmosphere. This process continues until an equilibrium is reached depending on the partial pressure of each specific gas in the atmosphere.

Types of Aerators

- Gravity aerators

- Fountain aerators

- Diffused aerators

- Mechanical aerators.

Gravity Aerators (Cascades): In gravity aerators, water is allowed to fall by gravity such that a large area of water is exposed to atmosphere, sometimes aided by turbulence.

Fountain Aerators : These are also known as spray aerators with special nozzles to produce a fine spray. Each nozzle is 2.5 to 4 cm diameter discharging about 18 to 36 l/h. Nozzle spacing should be such that each m3 of water has aerator area of 0.03 to 0.09 m2 for one hour.

Injection or Diffused Aerators : It consists of a tank with perforated pipes, tubes or diffuser plates, fixed at the bottom to release fine air bubbles from compressor unit. The tank depth is kept as 3 to 4 m and tank width is within 1.5 times its depth. If depth is more, the diffusers must be placed at 3 to 4 m

depth below water surface. Time of aeration is 10 to 30 min and 0.2 to 0.4 litres of air is required for 1 litre of water.

Mechanical Aerators: Mixing paddles as in flocculation are used. Paddles may be either submerged or at the surface.

## Iron and Manganese removal

Iron and manganese removal is the most common type of municipal water treatment. Iron and manganese occur naturally in water, especially groundwater. Neither of the elements causes adverse health effects; they are, in fact, essential to the human diet. However, water containing excessive amounts of iron and manganese can stain clothes, discolor plumbing fixtures, and sometimes add a “rusty” taste and look to the water.

## Methods in removal of Iron and Manganese

Phosphate Treatment Feeding Phosphate Solutions Removal By Ion Exchange Oxidation Using Aeration Oxidation With Chlorine

Oxidation With Permanganate

Operation Of Iron And Manganese Filter

## PHOSPHATE TREATMENT

In this treatment polyphosphate is added at the source to mask the effects of high iron concentrations in the distribution system. This is effective in cases in which the water contains up to 0.3 ppm of iron and less than 0.1 ppm of manganese.

## DEFLUORIDATION AND DEMINERALIZATION

Defluoridation

Method of water treatment that reduce the concentration of fluoride in the water, normally, in order to make it safe for human.

## Demineralization

A treatment process that removes dissolved minerals from water.

## Water softening

Water softening is the reduction of the concentrations of calcium, magnesium, and other ions in hard water.

Water softening methods mainly rely on the removal of Ca2+ and Mg2+ from a solution or the sequestration of these ions, i.e. binding them to a molecule that removes their ability to form scale or interfere with detergents. Removal is achieved by ion exchange and by precipitation methods. Sequestration entails the addition of chemical compounds called sequestration (or chelating) agents.Since Ca2+ and Mg2+ exist as nonvolatile salts, they can be removed by distilling the water, but distillation is too expensive in most cases (rainwater is soft because it is,

in effect, distilled).

## DESALINATION

Processes that remove some amount of salt and other minerals from water. More

## MEMBRANE SYSTEM

Membrane

A semi-permeable membrane is a VERY THIN film that allows some types of matter to pass through while leaving others behind.

## Types of Membranes

  - Membrane filtration.

  - Ultra filtration.

  - Nano filteration.

  - Reverse osmosis.

MEMBRANE PROCESSES

Common membrane processes include ultrafiltration (UF), reverse osmosis (RO), electrodialysis (ED), and electrodialysis reversal (EDR). These processes (with the exception of UF) reduce most ions; RO and UF systems also provide efficient reduction of nonionized organics and particulates. Because UF membrane porosity is too large for ion rejection, the UF process is used to reduce contaminants, such as oil and grease, and suspended solids.

## Reverse Osmosis

Osmosis is the flow of solvent through a semi-permeable membrane, from a dilute solution to a concentrated solution. This flow results from the driving force created by the difference in pressure between the two solutions. Osmotic pressure is the pressure that must be added to the concentrated solution side in order to stop the solvent flow through the membrane. Reverse osmosis is the process of reversing the flow, forcing water through a membrane from a concentrated solution to a dilute solution to produce filtered water. Reverse osmosis is created when sufficient pressure is applied to the concentrated solution to overcome the osmotic pressure. This pressure is provided by feed water pumps. Concentrated contaminants (brine) are reduced from the high-pressure side of the RO membrane, and filtered water (permeate) is reduced from the low-pressure side. Membrane modules may be staged in various design configurations, producing the highest-quality permeate with the least amount of waste.

Typically, 95% of dissolved salts are reduced from the brine. All particulates are removed. However, due to their molecular porosity, RO membranes do not remove dissolved gases, such as Cl2, CO2, and O2.

RO Membranes. The two most common RO membranes used in industrial water treatment are cellulose acetate (CA) and polyamide (PA) composite. Currently, most membranes are spiral wound; however, hollow fiber configurations are available. In the spiral wound configuration, a flat sheet membrane and spacers are wound around the permeate collection tube to produce flow channels for permeate and feed water. This design maximizes flow while minimizing the membrane module size.

Hollow fiber systems are bundles of tiny, hair-like membrane tubes. Ions are rejected when the feedwater permeates the walls of these tubes, and permeate is collected through the hollow center of the fibers. Concentrated brine is produced on the outside of the fibers contained by the module housing.

## Electrodialysis

Electrodialysis (ED) processes transfer ions of dissolved salts across membranes, leaving purified water behind. Ion movement is induced by direct current electrical fields. A negative elec-trode (cathode) attracts cations, and a positive electrode (anode) attracts anions. Systems are compartmentalized in stacks by alternating cation and anion transfer membranes. Alternating compartments carry concentrated brine and filtered permeate. Typically, 40-60% of dissolved ions are removed or rejected. Further improvement in water quality is obtained by staging (operation of stacks in series). ED processes do not remove particulate contaminants or weakly ionized contaminants, such as silica.

## Electrodialysis Reversal

Electrodialysis reversal (EDR) processes operate on the same principles as ED; however, EDR operation reverses system polarity (typically 3-4 times per hour). This reversal stops the buildup of concentrated solutions on the membrane and thereby reduces the accumulation of inorganic and organic deposition on the membrane surface. EDR systems are similar to ED systems, designed with adequate chamber area to collect both product water and brine. EDR produces water of the same quality as ED.

## Ultrafiltration

In many process and wastewater applications, reduction of dissolved ions is not required but efficient reduction of colloidal inorganic or organic molecules is. Ultrafiltration (UF) membrane configurations and system designs are similar to those used in the single-stage RO process. Because the large molecules removed by UF exhibit negligible osmotic pressure, operating pressures are usually much lower than in RO systems.

Typical applications include reduction of oil and grease and recovery of valuable contaminants in process waste streams.

## PRETREATMENT

Process is that rely on micro porous membranes must be protected from fouling.

Membrane foul-ing causes a loss of water production (flux), reduced permeate quality, and increased trans-membrane pressure drop.

Membrane fouling is typically caused by precipitation of inorganic salts, particulates of metal oxides, colloidal silt, and the accumulation or growth of microbiological organisms on the membrane surface. These fouling problems can lead to serious damage and necessitate more frequent replacement of membranes.

Membrane configurations and system designs are similar to those used in the single-stage RO process. Because the large molecules removed by UF exhibit negligible osmotic pressure, operating pressures are usually much lower than in RO systems.

Typical applications include reduction of oil and grease and recovery of valuable contaminants in process waste streams.

## SOLIDS REDUCTION

Membrane feed water should be relatively free from colloidal particulates. The most common particulates encountered in industrial membrane systems are silt, iron oxides, and manganese oxides. Silt Density Index (SDI) testing should be used to confirm sufficient water quality.